JS Air Curtains Essensse Neo

Air Curtain Specification Summary

- The Air Curtain shall have a self-supporting casing finished in RAL9010 as standard. Other RAL colours shall be available on request.

- The Air Curtain shall use low noise motor with tangential fans.

- The Air Curtain shall be available in a choice of sizes nominally 1.0m, 1.5m, 2.0m and 2.5m.

- The Air Curtain shall measure 252 mm high and 377mm deep.

- The unit shall be suitable for exposed mounting above a door using M6 threaded drop rods or by the supplied wall brackets.

- The inlet grille shall be perforated with filter function. For servicing, in normal environments, the grille only has to be periodically wiped or vacuumed.

- The outlet of the unit shall be adjustable.

- The Air Curtain shall be available with a choice of water or electric heating. For electric heating there will be a choice of standard or high heat output.

- Electrically heated units will use 400V 3 phase with power controls included.

- The Air Curtain will have a modular control system available in 2 versions – standard “Comfort” or advanced “Superior” controller.

- Both the “Comfort” and “Superior” controller shall have an intuitive to use touch screen display.

- Both controllers shall be available as master and slave variants. One master controller shall be capable of controlling up to 10 slave controllers.

- The master controller shall connect to the air curtain using standard 4 core screened control cable.

- All controllers shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- The “Comfort” controller shall have the following functionality: 3 speed fan selections, 2 electric heating levels, optional door contacts and optional room thermostat. Communication to a BMS or similar shall be possible using Modbus RTU.

- The “Superior” controller in addition to the features offered by the “Comfort” controller will offer automatic control with manual override. Electric heating will be controlled using pulse width modulation. Communication to a BMS or similar shall be possible using Modbus RTU or Modbus TCP.

- There shall be a volt free contact available for fault indication.

- Water heated units shall have the option of an external 3 port valve. The valve shall be controlled by the controller. For the “Comfort” controller this shall be on/off control. For the “Superior” controller this shall be a modulating valve.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858 656 			Fax: +44 (0) 1903 850 345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com