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JS Air Curtains Finesse Air Curtain Specification 


1. The Finesse is a discreet, high-performance air curtain built for installation in a suspended ceiling and has separated air intake and outlets to avoid circulation of air. Its self-supporting casing is made of galvanised plated steel.

2. The Finesse casing is finished with a structural epoxy-polyester paint finish, offered in RAL 9016 (White), with other RAL classic colours available on request. 

3. [bookmark: _Hlk221712899]As standard, the fans are ‘AC’ type with double inlet centrifugal design, featuring low noise levels. They use an external rotor motor, offer three selectable speeds, and come equipped with built-in thermal protection.

4. EC (electronically commutated) fans with low energy requirements can be specially ordered, offering enhanced energy efficiency, lower operating costs, and sophisticated control options.

5. The Finesse unit shall measure 304mm high by 639mm deep and can be supplied in various lengths ranging from 1.0m to 2.5m in 0.5m increments.

6. The unit is designed for easy recessed mounting in false ceilings using M8 threaded drop rods.

7. The air curtain may be installed “hard up” against non-flammable materials such as slab or steelwork above to enable installations in restricted ceiling voids, if required.

8. The air inlet and outlet lamellas are integrated into a single frame. For servicing, periodic cleaning or vacuuming of the grille is needed in normal conditions.

9. The unit can be specified with two regulated heating options: ‘E’ type (electric element heating with three stages), or ‘V’ type (LPHW water coil).

10. E’ type electric units shall operate on 400V/50Hz three-phase power and include power contactors, with two standard heating stages.

11. ‘V’ type water heated units shall offer on/off or proportional heating control, depending on optional valve type selected.

12. The Finesse is equipped with an ‘AirGenio Prime’ controller, featuring intuitive touch screen display, built-in temperature sensor, 7-day timer, volt free contact, and automatic control with manual override. The AirGenio application offers advanced settings and remote control functions.

13. The AirGenio Prime system supports master and slave operation, with one master unit capable of controlling up to 10 slave units. Each master unit shall be supplied with 20m of control cable.

14. Optional AirGenio Prime gateways shall be available for enhanced connectivity. BMS Gateway shall enable integration using Modbus TCP or BACnet protocols. Cloud Gateway shall allow Prime-controlled devices to be monitored, controlled and managed remotely through a web interface from any location.

15. The Finesse air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, is CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.


16. The system is to be supplied by					www:	Finesse Air Curtain
JS Air Curtains Limited 								
City Gates, 2-4 Southgate 
Chichester 								
West Sussex 							Tel:	+44 (0)333 038 4240
PO19 8DJ	 							e-mail:	sales@jsaircurtains.com
United Kingdom							Website:	www.jsaircurtains.com
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