JS Air Curtains Finesse VCF

Air Curtain Specification Summary

- The Air Curtain shall have a self-supporting casing made of steel. The grille will be finished in RAL9010 as standard. Other RAL colours shall be available on request.

- The Air Curtain shall use low noise centrifugal double inlet fans.

- The Air Curtain shall be available in a choice of 2 different fan powers to suit different mounting heights and environments.

- The fans shall be capable of 3 speed selections.

- The Air Curtain shall be available in a choice of sizes nominally 1.0m, 1.5m, 2.0m & 2.5m.

- The Air Curtain shall measure 304mm high and 639mm deep.

- The unit shall be suitable for ceiling recessed mounting using M8 threaded drop rods.

- The Air Curtain shall be capable of being installed “hard up” against non flammable materials such as slab / steelwork etc. above to enable installations in restricted ceiling voids if required.

- The inlet grille shall be perforated with filter function. For servicing, in normal environments, the grille only has to be periodically wiped or vacuumed.

- The Air Curtain shall be available with a choice of water or electric heating. Ambient unheated units shall be available on special request.

- Electrically heated units will use 400V 3 phase with power controls included.

- The Air Curtain will have a modular control system available in 2 versions – standard “Comfort” or advanced “Superior” controller.

- Both the “Comfort” and “Superior” controller shall have an intuitive to use touch screen display.

- Both controllers shall be available as master and slave variants. One master controller shall be capable of controlling up to 10 slave controllers.

- The “Comfort” controller shall have the following functionality: 3 speed fan selections, 2 electric heating levels, optional door contacts and optional room thermostat. Communication to a BMS or similar shall be possible using Modbus RTU.

- The “Superior” controller in addition to the features offered by the “Comfort” controller will offer automatic control with manual override. Electric heating will be controlled using pulse width modulation. Communication to a BMS or similar shall be possible using Modbus RTU or Modbus TCP.

- All controllers shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- There shall be a volt free contact available for fault indication.

- Water heated units shall have the option of an external 3 port valve. The valve shall be controlled by the controller. For the “Comfort” controller this shall be on/off control. For the “Superior” controller this shall be a modulating valve.

- The Air Curtain shall have the option of wall mounting or overhead mounting brackets.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858656 			Fax: +44 (0) 1903 850345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com