JS Air Curtains Max

Air Curtain Specification Summary

- The Air Curtain shall have a heavy casing made of double chamber aluminium profiles and hot galvanized plated steel panels, finished in RAL 9016 as standard. Other RAL colours shall be available on request.

- The Air Curtain shall use low noise axial fans driven by an external rotor motor with built-in thermal protection.

- The fans shall be capable of 5 speed selections.

- The Air Curtain shall be specifically designed for use on industrial doors.

- The Air Curtain shall be suitable for horizontal mounting over a door using M8 threaded drop rods or vertical mounting using a specially designed base plate.

- The Air Curtain shall be available in a choice of 5 sizes from 1,234mm to 3,542mm.

- It shall be possible to horizontally mount any number of units to cover the door opening width.

- It shall be possible to stack up to 2 units vertically using a specially designed joining kit to form a tower up to 7,194mm high including the base plate.

- The Air Curtain shall measure 660mm by 543mm in section.

- The Air Curtain shall be available with a choice of water, electric heating or ambient unheated.

- Water heated units will be available as standard with a choice of 2 coil types suitable for 80 or 60C flow.

- Electrically heated units will use 400V 3 phase, shielded elements with three heat settings with power contactors included.

- The Air Curtain will use anodised aluminium blow-out vanes, airfoil shaped, adjustable from 0 to 15º each side of vertical for airflow direction control.

- The Air Curtain shall include as standard a manual controller, 7m of telephonic cable with RJ45 (Plug & Play) connectors and a hand held infra-red remote.

- The manual controller shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- Electrically heated units shall be capable of accepting a thermostat connection which will act on the heater only, stopping the heater and allowing the fans to continue on reaching set point.

- Water heated units shall have the option of an external solenoid valve. The solenoid valve shall be switched by the controller.

- Optional controllers shall be available which will provide automatic control with manual override.

- Optional BMS Interface shall be available if required. This shall give the BMS direct control of the fan speed selection. In the case of an electrically heated unit the BMS shall have control of the heat settings. In the case of water heated units with optional solenoid valve the BMS shall be capable of switching the solenoid valve. All interfacing to the BMS will be done using volt free contacts.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858 656 			Fax: +44 (0) 1903 850345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com