JS Air Curtains Mini Optima

Air Curtain Specification Summary

- The Air Curtain shall have a self-supporting casing made of galvanized plated steel, finished in structural epoxy-polyester RAL 9016 as standard. Other RAL colours shall be available on request.

- The Air Curtain shall use low noise twisted cross-flow fans driven by an external rotor motor.

- The fans shall be capable of 2 speed selections.

- The Air Curtain shall be available in a choice of sizes nominally 1.0m, 1.5m & 2.0m.

- The Air Curtain shall measure 215mm high and 300mm deep including intake grille.

- The unit shall be suitable for exposed mounting above a door using M8 threaded drop rods.

- The inlet grille shall be micro-perforated with filter function. For servicing, in normal environments, the grille only has to be periodically wiped or vacuumed.

- The Air Curtain shall be available with a choice of water, electric heating or ambient unheated.

- Water heated units will be suitable for a nominal 80C flow.

- Electrically heated units will use 400V 3 phase, or 230V single phase shielded elements with two heat settings with power contactors included.

- The Air Curtain will use anodised aluminium blow-out vanes, airfoil shaped.

- The Air Curtain shall include as standard a manual controller, 7m of telephonic cable with RJ45 (Plug & Play) connectors and a hand held infra-red remote.

- The manual controller shall be capable of BMS/PLC/Timer etc. enable and disable by a suitable volt free contact.

- Electrically heated units shall be capable of accepting a thermostat connection which will act on the heater only, stopping the heater and allowing the fans to continue on reaching set point.

- Optional BMS Interface shall be available if required. This shall give the BMS direct control of the fan speed selection. In the case of an electrically heated unit the BMS shall have control of the heat settings. All interfacing to the BMS will be done using volt free contacts.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858 656 			Fax: +44 (0) 1903 850345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com