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JS Air Curtains Standesse XP Air Curtain Specification 


1. The Standesse XP is a powerful, yet elegant air curtain designed for horizontal installation, with a self-supporting galvanised steel casing.

2. The Standesse XP casing is finished with a structural epoxy-polyester paint finish, offered in standard RAL 9016 (White), with other RAL classic colours available on request. 

3. [bookmark: _Hlk221712899]The unit is equipped with unique Straw System Technology to maximise the screening effect. The Straw System ensures a laminar, compact and stable airflow across the entire exhaust nozzle.

4. The unit operates using EC (electronically commutated) double-inlet centrifugal fans driven by an external rotor motor and featuring low noise levels. With low energy requirements, the EC fans offer enhanced energy efficiency, lower operating costs, and sophisticated control options.

5. The Standesse XP unit shall measure 472mm high by 995mm deep and can be supplied in various lengths ranging from 1.0m to 3.0m in 0.5m increments.

6. The unit is designed for exposed, horizontal mounting above doors utilising M8 threaded drop rods. Optional brackets may be specially ordered for overhead or wall mounting, including, wall ‘rail’ supports.

7. The air inlet grille is perforated, with a 2 in 1 face filter that acts as a suction grille and filter to prevent particles from entering the air curtain. This removes the need to have a separate internal filter. Only routine cleaning or vacuuming is needed in normal conditions. 

8. The unit can be specified with two regulated heating options: ‘S’ type (low-energy air, unheated or recirculating ambient air) or ‘V’ type (LPHW water coil).

9. ‘V’ type water heated units offer either on/off, or proportional heating control, depending on optional valve type selected, with coil options for 60°, 70°C, 80°C or 90°C flow.

10. The Standesse XP is equipped with an AirGenio ‘Superior’ controller, featuring an advanced colour touch screen display, intuitive operation control, 3 fan speeds, volt free contact, and BMS connectivity options.

11. The AirGenio Superior system supports master and slave operation, with one master unit capable of controlling up to 10 slave units. Each master unit shall be supplied with 10m of control cable.

12. The Standesse XP air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, is CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.


13. The system is to be supplied by					www:	Standesse XP Air Curtain
JS Air Curtains Limited 								
City Gates, 2-4 Southgate 
Chichester 								
West Sussex 							Tel:	+44 (0)333 038 4240
PO19 8DJ	 							e-mail:	sales@jsaircurtains.com
United Kingdom							Website:	www.jsaircurtains.com
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