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JS Air Curtains VCP Air Curtain Specification 

1. The VCP is a heavy-duty industrial air curtain designed for vertical or horizontal installation, with self-supporting galvanised steel casing.

2. The VCP casing has a galvanised finish with the option of a RAL 9016 (White) paint finish. 

3. The unit is equipped with unique Straw System Technology to maximise the screening effect. The Straw System ensures a laminar, compact and stable airflow across the entire exhaust nozzle.

4. As standard, the VCP fans are ‘AC’ type. Low noise axial fans are driven by a 230V single phase motor, offer five selectable speeds, and come equipped with built-in thermal protection. 

5. EC (electronically commutated) fans with low energy requirements can be specially ordered, offering enhanced energy efficiency, lower operating costs, and sophisticated control options.

6. The VCP unit shall measure 521mm high by 551mm deep and can be supplied in lengths of 1.65m, 2.20m and 2.75m. 

7. The unit is suitable for exposed, horizontal mounting above door, hung using M8 threaded drop rods, or vertical mounting to the side of the doorway using a base plate with floor fixing points. Optional brackets may be specially ordered for overhead or wall mounting.

8. For larger doorways, up to six VCP units can be mounted horizontally to cover a width of up to 16.5m, or 3 units can be stacked vertically using a specially designed joining kit to form a tower up to 6.60m high.

9. The galvanised sheet casing and closed construction motors with self-lubricating ball bearings provide easy maintenance. Only routine cleaning or vacuuming is needed in normal conditions.

10. The unit can be specified with various regulated heating options: ‘S’ type (low-energy air only, unheated or recirculating ambient air), ‘E’ type (electric element heating with three stages), or ‘V’ type (LPHW water coil).

11. E’ type electric units shall operate on 400V/50Hz three-phase power and include power contactors, with two standard heating stages.

12. ‘V’ type water heated units shall offer on/off heating control with optional valve. 

13. The VCP is equipped as standard with an ‘AirGenio IC Prime’ digital controller, featuring 5 fan speeds, integrated timer, built-in temperature sensor, automatic antifreeze protection, and Modbus RTU compatibility with BMS. The AirGenio application offers advanced settings and remote control functions.

14. The AirGenio IC Prime system supports master and slave operation, with one master unit capable of controlling up to 6 slave units.

15. The VCP air curtain is produced to ISO 9001 standards, fully run tested for reliability, with traceable documentation for quality, is CE & UKCA certified and compliant with relevant regulations. BIM files can be provided upon request.


16. The system is to be supplied by					www:	VCP Air Curtain
JS Air Curtains Limited 								
City Gates, 2-4 Southgate 
Chichester 								
West Sussex 							Tel:	+44 (0)333 038 4240
PO19 8DJ	 							e-mail:	sales@jsaircurtains.com
United Kingdom							Website:	www.jsaircurtains.com
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