JS Air Curtains VCP Industrial

Air Curtain Specification Summary

- The Air Curtain will have a heavy duty steel casing with galvanised finish. A painted finish in RAL 9010 will also be available.

- The Air Curtain will use low noise axial fans driven by a 230V single phase motor with built-in thermal protection.

- The fans will be capable of 3 or 5 speed selections depending on controller selected.

- The Air Curtain will be specifically designed for use on industrial doors.

- The Air Curtain will be suitable for horizontal mounting over a door using M8 threaded drop rods or vertical mounting using a specially designed base plate and wall support brackets.

- The Air Curtain will be available in a choice of 3 sizes 1.65m, 2.20 & 2.75m.

- It will be possible to horizontally mount up to 6 units to cover a door opening width of up to 16.5m.

- It will be possible to stack up to 3 units vertically using a specially designed joining kit to form a tower up to 8.25m high.

- The Air Curtain will measure 521mm by 551mm in section.

- The Air Curtain will be available with a choice of water heating, electric heating or ambient unheated.

- Water heated units will be available with a coil suitable for up to 110C flow at a maximum operating pressure of 1.6MPa.

- The Air Curtain will be available with a range of controllers for 3 or 5 fan speed selections depending on application.

- ROVE controllers will provide simple, manual 5 speed fan control. Versions will be available to control up to 1 off unit.

- STRA1 controllers will provide manual 5 speed control with the provision to link to door contacts, timer, BMS etc... Controller will be of robust industrial construction with a rotary control knob. Versions will be available to control arrays up to 7.15m in length.

- RB1-7A controllers will provide manual 3 speed control with the provision to link to door contacts, timer, BMS etc... RB1-7A will be capable of controlling the optional solenoid valve. RB1-7A will be provided with a “touch pad” for ease of use. It will be possible to link up to 6 RB1-7A controllers to a single touch pad to control up to 6 off 2.75m long units.

- Water heated units will have the option of an external solenoid valve.

- The system is to be supplied by:

JS Air Curtains

Member of the Condair Group

Artex Avenue

Rustington

LITTLEHAMPTON

West Sussex

BN16 3LN

Tel: +44 (0) 1903 858 656 			Fax: +44 (0) 1903 850345

e-mail: sales@jsaircurtains.com		website: www.jsaircurtains.com